## Main Data
Default Storage Ring Refill Time |  |  | 0.25 | [16 empty] | Refill Timing in Days | 0.010417
Downtime for Run 2003-3
Fill # | Start | End | Length | Loss Reason | DIN # | Audit | Start | End | User Length | System Length | Cause | System | Group | Type | Description | Store Lost | Intention. Dump | Inhibits Beam | TOTAL
[5 empty] | 104593 |  | 2003-10-01 08:00 | 2003-10-01 08:03 | 0.05 | 0.05 | DIAG | DIAG | DIAG | Inhibits Beam to User | SR Orbit Correction [DIAG] |  |  | 1 | 1
1 | 2003-10-01 08:03 | 2003-10-01 11:40 | 3.6167 | Operator error [OPS] |  |  | 2003-10-01 11:40 | 2003-10-01 14:50 | 3.1667 | [9 empty] | 0
[5 empty] | 104591 |  | 2003-10-01 11:40 | 2003-10-01 12:10 |  | 0.5 | OPS | OPS | OPS | Store Lost | Operator error induced PSS trip [OPS] | 1 |  |  | 1
[5 empty] | 104591 |  | 2003-10-01 12:10 | 2003-10-01 12:37 |  | 0.45 | PS | PS | PS | Inhibits Beam to User | B:IK not available at beam loss [PS] |  |  | 1 | 1
[5 empty] | 104591 |  | 2003-10-01 12:37 | 2003-10-01 13:27 |  | 0.83333 | PS | PS | PS | Inhibits Beam to User | Booster corrector rampload problem [PS] |  |  | 1 | 1
[5 empty] | 104591 |  | 2003-10-01 13:27 | 2003-10-01 13:54 |  | 0.45 | DIAG | DIAG | DIAG | Inhibits Beam to User | Cleaning up SR orbit [DIAG] |  |  | 1 | 1
[7 empty] | 2003-10-01 13:54 | 2003-10-01 14:18 |  | 0.4 | OAG/software | Software | OAG | Inhibits Beam to User | Beam retained for less than hour |  |  | 1 | 1
[5 empty] | 104592 |  | 2003-10-01 14:18 | 2003-10-01 14:50 |  | 0.53333 | OAG/software | Software | OAG | Inhibits Beam to User | Beam lost during Steering "Undo" [OAG] |  |  | 1 | 1
3 | 2003-10-01 14:50 | 2003-10-02 17:48 | 26.9667 | S23 RTFB IOC error [CTL] | 104595 |  | 2003-10-02 17:48 | 2003-10-02 18:19 | 0.51667 | 0.51667 | CTL | CTL | CTL | Store Lost | Beam lost duringRTFB IOC recovery process | 1 |  |  | 1
6 | 2003-10-02 18:19 | 2003-10-02 22:04 | 3.75 | S9 EPS Trip [SI] |  |  | 2003-10-02 22:04 | 2003-10-02 23:59 | 1.9167 | [5 empty] | Beam restored, S9 EPS Trip again, fill restored |  |  |  | 0
[5 empty] | 104596 |  | 2003-10-02 22:04 | 2003-10-02 22:44 |  | 0.66667 | SI/Intlks | Beamline Intlks | SI | Store Lost | S9 EPS trip | 1 |  |  | 1
[7 empty] | 2003-10-02 22:44 | 2003-10-02 23:19 |  | 0.58333 | SI/Intlks | Beamline Intlks | SI | Inhibits Beam to User | Beam retained for less than hour |  |  | 1 | 1
[5 empty] | 104597 |  | 2003-10-02 23:19 | 2003-10-02 23:59 |  | 0.66667 | SI/Intlks | Beamline Intlks | SI | Inhibits Beam to User | 2nd S9 EPS trip |  |  | 1 | 1
8 | 2003-10-02 23:59 | 2003-10-03 15:21 | 15.3667 | SR-RF3 Crowbar Trip [Unknown] | 104599 |  | 2003-10-03 15:21 | 2003-10-03 15:40 | 0.31667 | 0.31667 | Unidentified | Unidentified | Unidentified | Store Lost | RF3 shut off during network storm [Unknown] | 1 |  |  | 1
9 | 2003-10-03 15:40 | 2003-10-04 04:28 | 12.8 | S9 EPS Trip [SI] | 104600 |  | 2003-10-04 04:28 | 2003-10-04 05:33 | 1.0833 | 1.0833 | SI/Intlks | Beamline Intlks | SI | Store Lost | Fault cleared, beam restored | 1 |  |  | 1
11 | 2003-10-04 05:33 | 2003-10-05 11:40 | 30.1167 | Water pump failure [ME] | 104601 |  | 2003-10-05 11:40 | 2003-10-05 12:33 | 0.88333 | 0.88333 | Water/ME | Water/ME | ME | Store Lost | S8 Absorber water flow trip caused by pump seizure | 1 |  |  | 1
14 | 2003-10-05 12:33 | 2003-10-05 22:03 | 9.5 | S9 EPS Trip [SI] | 104602 |  | 2003-10-05 22:03 | 2003-10-05 22:39 | 0.6 | 0.6 | SI/Intlks | Beamline Intlks | SI | Store Lost | Trip reset, beam restored | 1 |  |  | 1
16 | 2003-10-05 22:39 | 2003-10-06 15:59 | 17.3333 | Int Dump: End of Period |  |  | 2003-10-06 15:59 | 2003-10-06 15:59 | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 119.45 | [5 empty] | 8.5333 | 8.5333 | [8 empty] | 0
18 | 2003-10-07 08:00 | 2003-10-07 11:38 | 3.6333 | S9 EPS Trip [SI] | 104603 |  | 2003-10-07 11:38 | 2003-10-07 14:01 | 2.3833 | 2.3833 | SI/Intlks | Beamline Intlks | SI | Store Lost | The ASD-SI personnel found 2 loose fuses in the 9ID EPS rack; refill | 1 |  |  | 1
19 | 2003-10-07 14:01 | 2003-10-08 08:34 | 18.55 | Power bump/ComEd [Other] | 104605 |  | 2003-10-08 08:34 | 2003-10-08 09:01 | 0.45 | 0.45 | Other | Other | Other | Store Lost | Power bump/ ComEd | 1 |  |  | 1
20 | 2003-10-08 09:01 | 2003-10-11 08:36 | 71.5833 | S16:BH1 Glitch [PS] | 104607 |  | 2003-10-11 08:36 | 2003-10-11 08:51 | 0.25 | 0.25 | PS | PS | PS | Store Lost | S16B:H1 glitch | 1 |  |  | 1
21 | 2003-10-11 08:51 | 2003-10-13 07:59 | 47.1333 | Int Dump: End of Period |  |  | 2003-10-13 07:59 | 2003-10-13 07:59 | 0 |  | Scheduled | [5 empty] | 1 |  | 1
|  |  | 140.9 | [5 empty] | 3.0833 | 3.0833 | [8 empty] | 0
25 | 2003-10-15 08:00 | 2003-10-16 00:23 | 16.3833 | Vac. Valve Closure [CTL] | 104614 |  | 2003-10-16 00:23 | 2003-10-16 00:53 | 0.5 | 0.5 | CTL | CTL | CTL | Store Lost | Single Vacuum Valve closure [CTL] | 1 |  |  | 1
26 | 2003-10-16 00:53 | 2003-10-16 02:25 | 1.5333 | Cogging restart [DIAG] | 104615 |  | 2003-10-16 02:25 | 2003-10-16 02:49 | 0.4 | 0.4 | DIAG | DIAG | DIAG | Inhibits Beam to User | Gaps opened to restart cogging after IOCS11BPM reboot |  |  | 1 | 1
| 2003-10-16 02:49 | 2003-10-18 22:53 | 68.0667 | IOCS25FB [CTL] |  |  | 2003-10-18 22:53 | 2003-10-18 23:42 | 0.81667 | [9 empty] | 0
[5 empty] | 104617 |  | 2003-10-18 22:53 | 2003-10-18 23:23 |  | 0.5 | DIAG | DIAG | DIAG | Store Lost | DSP problem necessitated IOCSFB reboot resulting in lost beam | 1 |  |  | 1
[5 empty] | 104617 |  | 2003-10-18 23:23 | 2003-10-18 23:42 |  | 0.31667 | OAG/software | Software | OAG | Inhibits Beam to User | Beam was lost when RTFB loops initialized as the part of the IOC reboot procedure. |  |  | 1 | 1
27 | 2003-10-18 23:42 | 2003-10-21 08:00 | 56.3 | Int Dump: End of Period |  |  | 2003-10-21 08:00 | 2003-10-21 08:00 | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 142.2833 | [5 empty] | 1.7167 | 1.7167 | [8 empty] | 0
29 | 2003-10-21 16:00 | 2003-10-23 13:48 | 45.8 | S18/19 raw trip [PS] |  |  | 2003-10-23 13:48 | 2003-10-23 15:40 | 1.8667 | [9 empty] | 0
[5 empty] | 104623 |  | 2003-10-23 13:48 | 2003-10-23 14:52 |  | 1.0567 | PS | PS | PS | Store Lost | S18:19:R1 raw supply trip | 1 |  |  | 1
[5 empty] | 104623 |  | 2003-10-23 14:52 | 2003-10-23 15:40 |  | 0.81 | CTL | CTL | CTL | Inhibits Beam to User | S11 Local MPS fault inhibited injection into the SR |  |  | 1 | 1
30 | 2003-10-23 15:40 | 2003-10-27 07:59 | 89.3167 | Int Dump: End of Period |  |  | 2003-10-27 07:59 | 2003-10-27 07:59 | 0 |  | Scheduled | [5 empty] | 1 |  | 1
|  |  | 135.1167 | [5 empty] | 1.8667 | 1.8667 | [8 empty] | 0
31 | 2003-10-29 08:00 | 2003-10-31 04:25 | 44.4167 | SR valve closure [CTL] | 104630 |  | 2003-10-31 04:25 | 2003-10-31 04:50 | 0.41667 | 0.41667 | CTL | CTL | CTL | Store Lost | Single Vacuum Valve closure [CTL] | 1 |  |  | 1
32 | 2003-10-31 04:50 | 2003-11-03 15:59 | 83.15 | Int Dump: End of Period |  |  | 2003-11-03 15:59 | 2003-11-03 15:59 | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 127.5667 | [5 empty] | 0.41667 | 0.41667 | [8 empty] | 0
33 | 2003-11-04 08:00 | 2003-11-04 16:24 | 8.4 | PEM Steering Error [OAG] | 104634 |  | 2003-11-04 16:24 | 2003-11-04 16:41 | 0.28333 | 0.28333 | OAG/software | Software | OAG | Store Lost | PEM Steering Error [OAG] | 1 |  |  | 1
34 | 2003-11-04 16:41 | 2003-11-08 23:55 | 103.2333 | SR-RF4 Trip [RF] | 104639 |  | 2003-11-08 23:55 | 2003-11-09 00:15 | 0.33333 | 0.33333 | RF | RF | RF | Store Lost | Power monitor trip [RF] | 1 |  |  | 1
35 | 2003-11-09 00:15 | 2003-11-09 01:34 | 1.3167 | UPS Fault [IT] | 104640 |  | 2003-11-09 01:34 | 2003-11-09 11:18 | 9.7333 | 9.7333 | IT/Network | Network | IT | Store Lost | UPS Fault [IT] | 1 |  |  | 1
36 | 2003-11-09 11:18 | 2003-11-10 00:09 | 12.85 | UPS Fault [IT] | 104641 |  | 2003-11-10 00:09 | 2003-11-10 06:41 | 6.5333 | 6.5333 | IT/Network | Network | IT | Store Lost | UPS Fault [IT] | 1 |  |  | 1
37 | 2003-11-10 06:41 | 2003-11-10 08:59 | 2.3 | Int Dump: End of Period |  |  | 2003-11-10 08:59 | 2003-11-10 08:59 | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 128.1 | [5 empty] | 16.8833 | 16.8833 | [8 empty] | 0
39 | 2003-11-12 08:00 | 2003-11-12 23:14 | 15.2333 | IOCS25FB Hung Task [DIA] | 104643 |  | 2003-11-12 23:14 | 2003-11-12 23:38 | 0.4 | 0.4 | DIAG | DIAG | DIAG | Store Lost | Beam lost during reboot, refilled SR [DIA] | 1 |  |  | 1
41 | 2003-11-12 23:38 | 2003-11-13 22:17 | 22.65 | SR Gate Valve [CTL] | 104644 |  | 2003-11-13 22:17 | 2003-11-13 22:40 | 0.38333 | 0.38333 | CTL | CTL | CTL | Store Lost | SR gate Valve VM:02:VV02 closed, refill [CTL] | 1 |  |  | 1
44 | 2003-11-13 22:40 | 2003-11-17 13:09 | 86.4833 | 22ID EPS trip [SI] | 104647 |  | 2003-11-17 13:09 | 2003-11-17 14:07 | 0.96667 | 0.96667 | SI/Intlks | Beamline Intlks | SI | Store Lost | Recover from EPS trip, refill [SI] | 1 |  |  | 1
52 | 2003-11-17 14:07 | 2003-11-18 07:59 | 17.8667 | Int Dump: End of Period |  |  | 2003-11-18 07:59 | 2003-11-18 07:59 | 0 |  | Scheduled |  | CTL |  |  |  | 1 |  | 1
|  |  | 142.2333 | [5 empty] | 1.75 | 1.75 | [8 empty] | 0
54 | 2003-11-18 16:00 | 2003-11-24 06:57 | 134.95 | UPS AC breaker trip [IT] |  |  | 2003-11-24 06:57 | 2003-11-24 10:41 | 3.7333 | [9 empty] | 0
[5 empty] | 104650 |  | 2003-11-24 06:57 | 2003-11-24 10:23 |  | 3.4333 | IT/Network | Network | IT | Store Lost | UPS AC Breaker Trip [IT] | 1 |  |  | 1
[5 empty] | 104650 |  | 2003-11-24 10:23 | 2003-11-24 10:41 |  | 0.3 | DIAG | DIAG | DIAG | Inhibits Beam to User | RT Feedback problem [DIA] |  |  | 1 | 1
55 | 2003-11-24 10:41 | 2003-11-24 14:37 | 3.9333 | S32/33 Raw PS Trip [ES] | 104651 |  | 2003-11-24 14:37 | 2003-11-24 15:18 | 0.68333 | 0.68333 | PS | PS | PS | Store Lost | S32/33 Raw PS trip, reset, conditioning, refill [ES] | 1 |  |  | 1
56 | 2003-11-24 15:18 | 2003-11-25 07:59 | 16.6833 | Int Dump: End of Period |  |  | 2003-11-25 07:59 | 2003-11-25 07:59 | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 155.5667 | [5 empty] | 4.4167 | 4.4167 | [8 empty] | 0
57 | 2003-11-25 16:00 | 2003-11-26 23:59 | 31.9833 | Int Dump: End of Period |  |  | 2003-11-26 23:59 | 2003-11-26 23:59 | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 31.9833 | [5 empty] | 0 | 0 | [8 empty] | 0
58 | 2003-11-28 08:00 | 2003-11-29 04:04 | 20.0667 | SR-RF4 pwr mon trip [RF] | 104656 |  | 2003-11-29 04:04 | 2003-11-29 04:30 | 0.43333 | 0.43333 | RF | RF | RF | Store Lost | RF 4 tripped on an ion gauge fault Cavity #1 Sector 40 [RF] | 1 |  |  | 1
59 | 2003-11-29 04:30 | 2003-12-02 16:00 | 83.5 | Int Dump: End of Period |  |  | 2003-12-02 16:00 | 2003-12-02 16:00 | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 103.5667 | [5 empty] | 0.43333 | 0.43333 | [8 empty] | 0
64 | 2003-12-04 08:00 | 2003-12-05 12:21 | 28.35 | BPLD Trip [Unknown] | 104657 |  | 2003-12-05 12:21 | 2003-12-05 12:48 | 0.45 | 0.45 | Unidentified | Unidentified | Unidentified | Store Lost | Unknown cause, still under investigation | 1 |  |  | 1
65 | 2003-12-05 12:48 | 2003-12-09 06:30 | 89.7 | S22 Converter Trip [PS] | 104658 |  | 2003-12-09 06:30 | 2003-12-09 08:00 | 1.5 | 1.5 | PS | PS | PS | Store Lost | Five power supplies in S22 tripped,, beam retained less than 1 hr. [PS] | 1 |  |  | 1
|  |  | 118.05 | [5 empty] | 1.95 | 1.95 | [8 empty] | 0
67 | 2003-12-09 16:00 | 2003-12-09 22:34 | 6.5667 | Rad.Mon. fault [UES] | 104662 |  | 2003-12-09 22:34 | 2003-12-09 23:09 | 0.58333 | 0.58333 | UES/Intlk | Intlk/Rad | UES | Store Lost |  | 1 |  |  | 1
68 | 2003-12-09 23:09 | 2003-12-11 21:34 | 46.4167 | 34ID PSS trip [SI] | 104665 |  | 2003-12-11 21:34 | 2003-12-11 22:16 | 0.7 | 0.7 | SI/Intlks | Beamline Intlks | SI | Store Lost | 34ID PSS trip [SI] | 1 |  |  | 1
69 | 2003-12-11 22:16 | 2003-12-13 05:19 | 31.05 | S17BQ4 PS fault [PS] | 104666 |  | 2003-12-13 05:19 | 2003-12-13 06:36 | 1.2833 | 1.2833 | PS | PS | PS | Store Lost | S17BQ4 PS fault and swapout [PS] | 1 |  |  | 1
70 | 2003-12-13 06:36 | 2003-12-15 15:59 | 57.3833 | Int Dump: End of Period |  |  | 2003-12-15 15:59 | 2003-12-15 15:59 | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 141.4167 | [5 empty] | 2.5667 | 2.5667 | [8 empty] | 0
72 | 2003-12-16 08:00 | 2003-12-22 | 136 | Int Dump: End of Period |  |  | 2003-12-22 | 2003-12-22 | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 136 | [5 empty] | 0 | 0 | [8 empty] | 0
|  | Number of Lost Fills | 29 | [5 empty] | Downtime
|  | Number of Intentional Dumps | 12 | [5 empty] | User | System
|  | Number of Fills | 41 | [5 empty] | 43.6167 | 43.6167 | [5 empty] | 29 | 12 | 12 | 53
[16 empty] | SL | Scheduled | Inhibits
|  | Total User Beam | 1622.3833 | 67.5993 | User Beam days | [13 empty] | 67
|  | Total User Downtime | 43.6167 | <-- This downtime includes Gaps Open
|  | Total Schedule Run Length | 1666
41
|  | Mean Time Between Faults | 55.9443
|  | Faults/Day of Delivered Beam | 0.429 | [13 empty] | #REF!
|  | X-ray Availability | 97.38%
2