## Main Data
Default Storage Ring Refill Time |  |  | 0.25 | [16 empty] | Refill Timing in Days | 0.010417
Downtime for Run 2006-3
Fill # | Start | End | Length | Loss Reason | DIN # | Audit | Start | End | User Length | System Length | Cause | System | Group | Type | Description | Store Lost | Intention. Dump | Inhibits Beam | TOTAL
|  |  | 0 | RF3 switch to Booster | 105170 |  | 2006-10-03 08:00 | 2006-10-03 12:31 | 4.5167 | 4.5167 | RF | RF | RF | Inhibits beam to user | RF3 switch to Booster,disable RF4 temp intlk [RF] |  |  | 1 | 1
1 | 2006-10-03 12:31 | 2006-10-04 14:11 | 25.6667 | ACIS tripped to NSV [SI] | 105171 |  | 2006-10-04 14:11 | 2006-10-04 15:02 | 0.85 | 0.85 | SI | SI | SI | Store Lost | Incorrect jumper applied[SI], refill | 1 |  |  | 1
2 | 2006-10-04 15:02 | 2006-10-10 08:00 | 136.9667 | Int Dump: End of Period |  |  |  |  | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 162.6333 | [5 empty] | 5.3667 | 5.3667 | [8 empty] | 0
3 | 2006-10-11 08:00 | 2006-10-11 15:38 | 7.6333 |  | 105177 |  | 2006-10-11 15:38 | 2006-10-11 16:37 | 0.98333 | 0.98333 | UNK | UNK | UNK | Store Lost |  | 1 |  |  | 1
5 | 2006-10-11 16:37 | 2006-10-14 18:59 | 74.3667 | S39 MPS Latch card [CTL] | 105179 |  | 2006-10-14 18:59 | 2006-10-14 19:18 | 0.31667 | 0.31667 | CTL | CTL | CTL | Store Lost |  | 1 |  |  | 1
6 | 2006-10-14 19:18 | 2006-10-15 03:19 | 8.0167 | BPM glitch [DIAG] | 105180 |  | 2006-10-15 03:19 | 2006-10-15 06:22 | 3.05 | [9 empty] | 0
[7 empty] | 2006-10-15 03:19 | 2006-10-15 03:49 |  | 0.5 | DIA | DIA | DIA | Store Lost |  | 1 |  |  | 1
[7 empty] | 2006-10-15 03:49 | 2006-10-15 06:22 |  | 2.55 | SI | SI | SI | Inibits beam to user | 31ID SS not closed 2.54 hr. [SI] |  |  |  | 0
7 | 2006-10-15 06:22 | 2006-10-17 08:00 | 49.6333 | Int Dump: End of Period |  |  |  |  | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 139.65 | [5 empty] | 4.35 | 4.35 | [8 empty] | 0
8 | 2006-10-18 08:00 | 2006-10-23 08:00 | 120 | Int Dump: End of Period |  |  |  |  | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 120 | [5 empty] | 0 | 0 | [8 empty] | 0
9 | 2006-10-25 08:00 | 2006-10-31 08:00 | 145 | Int Dump: End of Period |  |  |  |  | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 145 | [5 empty] | 0 | 0 | [8 empty] | 0
10 | 2006-11-01 08:00 | 2006-11-03 20:50 | 60.8333 | S36/37 Cav. Pwr Loss[RF] | 105193 |  | 2006-11-03 20:50 | 2006-11-03 21:17 | 0.45 | 0.45 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
11 | 2006-11-03 21:17 | 2006-11-04 00:58 | 3.6833 | 21ID FEEPS Flw fault[SI] | 105194 |  | 2006-11-04 00:58 | 2006-11-04 03:35 | 2.6167 | 2.6167 | SI | SI | SI | Store Lost | Reset PLC backplane, refill | 1 |  |  | 1
12 | 2006-11-04 03:35 | 2006-11-05 02:42 | 23.1167 | 21ID FEEPS Flw fault[SI] | 105195 |  | 2006-11-05 02:42 | 2006-11-05 03:36 | 0.9 | 0.9 | SI | SI | SI | Store Lost | Reset PLC backplane, refill | 1 |  |  | 1
13 | 2006-11-05 03:36 | 2006-11-07 08:00 | 52.4 | Int Dump: End of Period |  |  |  |  | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 140.0333 | [5 empty] | 3.9667 | 3.9667 | [8 empty] | 0
14 | 2006-11-08 08:00 | 2006-11-08 11:14 | 3.2333 | S20:21 Raw P.S. trip[PS] | 105198 |  | 2006-11-08 11:14 | 2006-11-08 12:07 | 0.88333 | 0.88333 | PS | PS | PS | Store Lost | Replaced relay in raw PS, refill | 1 |  |  | 1
15 | 2006-11-08 12:07 | 2006-11-13 08:00 | 115.8833 | Int Dump: End of Period |  |  |  |  | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 119.1167 | [5 empty] | 0.88333 | 0.88333 | [8 empty] | 0
16 | 2006-11-15 08:00 | 2006-11-16 00:05 | 16.0833 | Beam Instability [OA] | 105200 |  | 2006-11-16 00:05 | 2006-11-16 00:30 | 0.41667 | [9 empty] | 0
[7 empty] | 2006-11-16 00:05 | 2006-11-16 00:17 |  | 0.2 | OA | OA | OA | Store Lost |  | 1 |  |  | 1
[7 empty] | 2006-11-16 00:17 | 2006-11-16 00:30 |  | 0.21667 | PHY | PHY | PHY | Inibits beam to user |  |  |  |  | 0
17 | 2006-11-16 00:30 | 2006-11-16 05:31 | 5.0167 | Beam instability [PHY] | 105202 |  | 2006-11-16 05:31 | 2006-11-16 08:03 | 2.5333 | [9 empty] | 0
[7 empty] | 2006-11-16 05:31 | 2006-11-16 06:47 |  | 1.2667 | PHY | PHY | PHY | Store Lost |  | 1 |  |  | 1
[7 empty] | 2006-11-16 06:47 | 2006-11-16 08:03 |  | 1.2667 | OA | OA | OA | Inibits beam to user |  |  |  |  | 0
19 | 2006-11-16 08:03 | 2006-11-19 18:50 | 82.7833 | Under Investigation | 105203 |  | 2006-11-19 18:50 | 2006-11-19 19:14 | 0.4 | 0.4 | UNK | UNK | UNK | Store Lost |  | 1 |  |  | 1
20 | 2006-11-19 19:14 | 2006-11-20 13:36 | 18.3667 | Under Investigation | 105205 |  | 2006-11-20 13:36 | 2006-11-20 14:15 | 0.65 | 0.65 | UNK | UNK | UNK | Store Lost |  | 1 |  |  | 1
21 | 2006-11-20 14:15 | 2006-11-21 00:50 | 10.5833 | Under Investigation | 105206 |  | 2006-11-21 00:50 | 2006-11-21 01:06 | 0.26667 | 0.26667 | UNK | UNK | UNK | Store Lost |  | 1 |  |  | 1
22 | 2006-11-21 01:06 | 2006-11-23 | 46.9 | Int Dump: End of Period |  |  |  |  | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 179.7333 | [5 empty] | 4.2667 | 4.2667 | [8 empty] | 0
23 | 2006-11-24 08:00 | 2006-11-28 08:00 | 96 | Int Dump: End of Period |  |  |  |  | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 96 | [5 empty] | 0 | 0 | [8 empty] | 0
24 | 2006-11-29 08:00 | 2006-12-03 23:29 | 111.4833 | Under Investigation | 105209 |  | 2006-12-03 23:29 | 2006-12-03 23:52 | 0.38333 | 0.38333 | UNK | UNK | UNK | Store Lost |  | 1 |  |  | 1
25 | 2006-12-03 23:52 | 2006-12-05 08:00 | 32.1333 | Int Dump: End of Period |  |  |  |  | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 143.6167 | [5 empty] | 0.38333 | 0.38333 | [8 empty] | 0
26 | 2006-12-06 08:00 | 2006-12-12 08:00 | 144 | Int Dump: End of Period |  |  |  |  | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 144 | [5 empty] | 0 | 0 | [8 empty] | 0
27 | 2006-12-13 08:00 | 2006-12-15 12:54 | 52.9 | Network Storm [IT] | 105211 |  | 2006-12-15 12:54 | 2006-12-15 15:36 | 2.7 | 2.7 | IT | IT | IT | Store Lost |  | 1 |  |  | 1
28 | 2006-12-15 15:36 | 2006-12-18 18:00 | 74.4 | RF4 HVPS trip {RF] | 105212 |  | 2006-12-18 18:00 | 2006-12-18 19:31 | 1.5167 | [5 empty] | RF4 trip,0.5hr[RF];wrong cath. volt.,1.01hr[OA] |  |  |  | 0
[7 empty] | 2006-12-18 18:00 | 2006-12-18 18:30 |  | 0.5 | RF | RF | RF | Store Lost |  | 1 |  |  | 1
[7 empty] | 2006-12-18 18:30 | 2006-12-18 19:31 |  | 1.0167 | OA | OA | OA | Inibits beam to user |  |  |  |  | 0
29 | 2006-12-18 19:31 | 2006-12-19 04:30 | 8.9833 | S38 HOM trip [RF] | 105213 |  | 2006-12-19 04:30 | 2006-12-19 06:48 | 2.3 | 2.3 | RF | RF | RF | Store Lost | Fixed loose RTD connection, refilled | 1 |  |  | 1
30 | 2006-12-19 06:48 | 2006-12-20 00:05 | 17.2833 | Int Dump: End of Period |  |  |  |  | 0 | 0 | Scheduled | [5 empty] | 1 |  | 1
|  |  | 153.5667 | [5 empty] | 6.5167 | 6.5167 | [8 empty] | 0
|  | Number of Lost Fills | 17 | [5 empty] | Downtime
|  | Number of Intentional Dumps | 11 | [5 empty] | User | System
|  | Number of Fills | 28 | [5 empty] | 25.7333 | 25.7333 | [5 empty] | 17 | 11 | 1 | 29
[16 empty] | SL | Scheduled | Inhibits
|  | Total User Beam | 1543.35 | 64.3062 | User Beam days
|  | Total User Downtime | 25.7333 | <-- This downtime includes Gaps Open
|  | Total Schedule Run Length | 1569.0833
28
|  | Mean Time Between Faults | 90.7853
|  | Faults/Day of Delivered Beam | 0.26436 | [13 empty] | #REF!
|  | X-ray Availability | 98.36% | [13 empty] | #REF!
2

## Stats
Group
Data | CTL | PS | RF | UNK | SI | DIA | OA | PHY | IT | Grand Total
Sum of Inhibits Beam | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Sum of Intention. Dump | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sum of Store Lost | 1 | 1 | 3 | 5 | 3 | 1 | 1 | 1 | 1 | 17
Sum of System Length | 0.31667 | 0.88333 | 7.7667 | 2.6833 | 6.9167 | 0.5 | 2.4833 | 1.4833 | 2.7 | 25.7333
| RF | Diag | PS | Controls | Accelerator Intlks | Beamline Intlks | Radiation Intlks | Water/ME | Operations | Physics | ID-FE | Electrical-APS | Electrical-ANL | Cooling-ANL | Other | Network | Unidentified | Grand Total | Total Hours
Hours for Run | 7.7667 | 0.5 | 0.88333 | 0.31667 |  | 6.9167 |  |  | 2.4833 | 1.4833 | [5 empty] | 2.7 | 2.6833 | 25.7333
Run 2006-3 | 0.495% | 0.03187% | 0.0563% | 0.02018% |  | 0.4408% |  |  | 0.1583% | 0.09454% | [5 empty] | 0.1721% | 0.171% | 1.64%
Budget | 0.54% | 0.12% | 0.54% | 0.3% | 0.06% | 0.06% | 0.06% | 0.36% | 0.12% | 0% | 0.06% | 0.06% | 0.18% | 0.06% | 0.18% | 0.12% | 0.06% | 3%
Faults | 3 | 1 | 1 | 1 |  | 3 |  |  | 1 | 1 | [5 empty] | 1 | 5 | 17
| RF | Diag | PS | Controls | Accelerator Intlks | Beamline Intlks | Radiation Intlks | MOM | Operations | Physics | ID-FE | Electrical-APS | Electrical-ANL | Cooling-ANL | Other | Network | Unidentified
Run 2006-3 | 0.046652 | 0.015551 | 0.015551 | 0.015551 | 0 | 0.046652 | 0 |  | 0.015551 | 0.015551 | 0 |  | 0 |  |  | 0.015551 | 0.077753 | 0.26436
Budget | 0.12 | 0.03 | 0.12 | 0.05 | 0.01 | 0.01 | 0.02 | 0.06 | 0.02 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.02 | 0.53
Total User Beam | Group CTL: 1543.35
Total Schedule Run Length | Group CTL: 1569.0833